## MBMS資料表
Index | tag | name | tagType | error | unit | round | plotType | y_title | bitIndex | bitName | translate | color | alarm | Data | EMS | 名稱備註
1 | heartbeat | H_Beat | number | --- | dec | 0 | [7 empty] | System Heartbeat | ! | 系統心跳
2 | count_string_svc | SVC[EA] | number | --- | dec | 0 | [7 empty] | Count of String in SVC | V(保固)(一個月) | 服務String數
3 | count_string_sys | Total[EA] | number | --- | dec | 0 | [7 empty] | Count of String in Total | V(保固)(一個月) | 系統String數
4 | i_svc | SVC[A] | number | --- | A | 0 | scatter | 電流(A) | [5 empty] | SVC Current (Connected) | V(保固)(一年) | 服務總電流
5 | v_svc | SVC[V](Avg) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | SVC Voltage (Connected) (Average) | V(保固)(一年) | 服務總電壓(平均值)
6 | v_mid_svc | SVC[V](Mid) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | SVC Voltage (Connected) (Median) | V | 服務總電壓(中位數)
7 | v_max_svc | SVC[V](Max) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | SVC Voltage (Connected) (Maximum) | V | 服務總電壓(最大值)
8 | v_min_svc | SVC[V](Min) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | SVC Voltage (Connected) (Minimum) | V | 服務總電壓(最小值)
9 | soc_svc | SVC[%](Avg) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | SVC SOC (Connected) (Average) | V(保固)(一年) | 服務總SOC(平均值)
10 | soc_mid_svc | SVC[%](Mid) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | SVC SOC (Connected) (Median) | V | 服務總SOC(中位數)
11 | soc_max_svc | SVC[%](Max) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | SVC SOC (Connected) (Maximum) | V | 服務總SOC(最大值)
12 | soc_min_svc | SVC[%](Min) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | SVC SOC (Connected) (Minimum) | V | 服務總SOC(最小值)
13 | i_sys | SYS[A] | number | --- | A | 0 | scatter | 電流(A) | [5 empty] | System Current | V | 系統總電流
14 | v_sys | SYS[V](Avg) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | System Voltage (Average) | V | 系統總電壓(平均值)
15 | v_mid_sys | SYS[V](Mid) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | System Voltage (Median) | V | 系統總電壓(中位數)
16 | v_max_sys | SYS[V](Max) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | System Voltage (Maximum) | V | 系統總電壓(最大值)
17 | v_min_sys | SYS[V](Min) | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | System Voltage (Minimum) | V | 系統總電壓(最小值)
18 | soc_sys | SOC[%](Avg) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | System SOC (Average) | V | 系統總SOC(平均值)
19 | soc_mid_sys | SOC[%](Mid) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | System SOC (Median) | V | 系統總SOC(中位數)
20 | soc_max_sys | SOC[%](Max) | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | System SOC (Maximum) | V | 系統總SOC(最大值)
21 | soc_min_sys | SOC[%](Min) | number | --- | % | 1 | scatter | SOH(%) | [5 empty] | System SOC (Minimum) | V | 系統總SOC(最小值)
22 | soh_sys | SOH[%](Avg) | number | --- | % | 1 | scatter | SOH(%) | [5 empty] | System SOH (Average) | V | 系統總SOH(平均值)
23 | soh_mid_sys | SOH[%](Mid) | number | --- | % | 1 | scatter | SOH(%) | [5 empty] | System SOH (Median) | V | 系統總SOH(中位數)
24 | soh_max_sys | SOH[%](Max) | number | --- | % | 1 | scatter | SOH(%) | [5 empty] | System SOH (Maximum) | V | 系統總SOH(最大值)
25 | soh_min_sys | SOH[%](Min) | number | --- | % | 1 | scatter | SOH(%) | [5 empty] | System SOH (Minimum) | V | 系統總SOH(最小值)
26 | cv_max_sys | [CV](Max) | number | --- | V | 3 | scatter | 電壓(V) | [5 empty] | System Cell Voltage (Maximum) | V | 系統最高單電池電壓(#電池櫃)
27 | cv_max_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Voltage (Maximum) Rack Position | V
28 | cv_min_sys | [CV](Min) | number | --- | V | 3 | scatter | 電壓(V) | [5 empty] | System Cell Voltage (Minimum) | V | 系統最低單電池電壓(#電池櫃)
29 | cv_min_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Voltage (Minimum) Rack Position | V
30 | cv_diff_sys | [CV](Max_Diff) | number | --- | V | 3 | scatter | 電壓(V) | [5 empty] | System Cell Voltage (Maximum Difference) | V | 系統最高單電池電壓差(#電池櫃)
31 | cv_diff_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Voltage (Maximum Difference) Rack Position | V
32 | ct_max_sys | [CT](Max) | number | --- | ℃ | 2 | scatter | 電壓(V) | [5 empty] | System Cell Temperature (Maximum) | V(保固)(一年) | 系統最高單電池溫度(#電池櫃)
33 | ct_max_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Temperature (Maximum) Rack Position | V
34 | ct_min_sys | [CT](Min) | number | --- | ℃ | 2 | scatter | 溫度(°C) | [5 empty] | System Cell Temperature (Minimum) | V(保固)(一年) | 系統最低單電池溫度(#電池櫃)
35 | ct_min_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Temperature (Minimum) Rack Position | V
36 | ct_diff_sys | [CT](Max_Diff) | number | --- | ℃ | 2 | scatter | 溫度(°C) | [5 empty] | System Cell Temperature (Maximum Difference) | V | 系統最高單電池溫度差(#電池櫃)
37 | ct_diff_rIndex_sys | Loc[R#] | number | --- | dec | 0 | [7 empty] | System Cell Temperature (Maximum Difference) Rack Position | V
38 | i_chg_limit_svc | Limit[A](Chg) | number | --- | A | 1 | scatter | 電流(A) | [5 empty] | SVC Current Limit of Charge | V | 服務充電電流限制
39 | i_dischg_limit_svc | Limit[A](Dchg) | number | --- | A | 1 | scatter | 電流(A) | [5 empty] | SVC Current Limit of Discharge | V | 服務放電電流限制
40 | p_chg_limit_svc | Limit[kW](Chg) | number | --- | kW | 2 | scatter | 功率(kW) | [5 empty] | SVC Power Limit of Charge | V(保固)(一個月) | 服務充電功率限制
41 | p_dischg_limit_svc | Limit[kW](Dchg) | number | --- | kW | 2 | scatter | 功率(kW) | [5 empty] | SVC Power Limit of Discharge | V(保固)(一個月) | 服務放電功率限制
42 | kwh_chg_sys | Total[kWh](Chg) | number | --- | kWh | 3 | bar | 電能(kWh) | [5 empty] | System Accumulation Amount of Charge Power | V(保固)(一年) | 系統充電電能
43 | kwh_dischg_sys | Total[kWh](Dchg) | number | --- | kWh | 3 | bar | 電能(kWh) | [5 empty] | System Accumulation Amount of Discharge Power | V(保固)(一年) | 系統放電電能
44 | v_ref_sys | Partial_Ref[V] | number | --- | V | 1 | scatter | 電壓(V) | [5 empty] | [Partial Operation] System Reference Voltage | V | 系統電壓參考值(#電池櫃)
45 | v_ref_rIndex_sys | Partial_Ref[R#] | number | --- | dec | 0 | [7 empty] | [Partial Operation] System Reference Voltage Rack Position | V
46 | status_sys | [System Command] | bits | --- |  |  |  |  | 0 | [Command] All DC Contactor Open | "0":"False","1":"True" |  |  | System Command Status | V | 系統狀態
| status_sys | [System Command] | bits | --- |  |  |  |  | 1 | [Command] All DC Contactor Close | "0":"False","1":"True" |  |  |  | V
| status_sys | [System Command] | bits | --- |  |  |  |  | 2 | [Command] Protection Reset | "0":"False","1":"True" |  |  |  | V
| status_sys | [System Command] | bits | --- |  |  |  |  | 3 | [Command] System Protection | "0":"False","1":"True" |  |  |  | V
47 | mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 0 | [Initialize] | "0":"False","1":"True" |  |  | System Mode #1 | V(保固)(一個月) | 系統模式1
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 1 | [Offline] Normal_Operating | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 2 | [Offline] Partial_Operating | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 3 | [Offline] System_Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 4 | [Online] Normal_Operating | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 5 | [Online] Partial_Operating | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 7 | [E-Stop] | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 8 | [Progress] Internal Function | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 14 | Charge Mode | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode1_sys | [System Mode#1] | bits | --- |  |  |  |  | 15 | Discharge Mode | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
48 | mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 8 | [Rack Powerline Wiring Check] Initialize | "0":"False","1":"True" |  |  | System Alarm #2 | V(保固)(一個月) | 系統模式2
| mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 9 | [Rack Powerline Wiring Check] Ready | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 10 | [Rack Powerline Wiring Check] Check #1 | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 11 | [Rack Powerline Wiring Check] Check #2 | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 12 | [Rack Powerline Wiring Check] Complete | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| mode2_sys | [System Mode#2] | bits | --- |  |  |  |  | 13 | [Rack Powerline Wiring Check] Failure | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
49 | alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 0 | [Partial Operation] Notice | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[Partial Operation] Notice","level":1,"protection":2} | System Alarm #1 | V(保固)(一個月) | 電池櫃告警1
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 1 | [Partial Operation] Alarm | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[Partial Operation] Alarm","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 2 | [Partial Operation] System Stop | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[Partial Operation] System Stop","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 3 | [E-Stop] Partial Operation | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[E-Stop] Partial Operation","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 4 | [E-Stop] Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[E-Stop] Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 5 | [E-Stop] SPD | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[E-Stop] SPD","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 6 | [E-Stop] Permanent Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[E-Stop] Permanent Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 14 | [DS Operation] Trip | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[DS Operation] Trip","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_sys | [System Alarm#1] | bits | --- |  |  |  |  | 15 | [Initialize] Need Commissioning | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"[Initialize] Need Commissioning","level":1,"protection":2} |  | V(保固)(一個月)
48 | alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 0 | Disconnect RTU Alarm | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect RTU Alarm","level":1,"protection":2} | System Alarm #2 | V(保固)(一個月) | 系統告警2
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 1 | Disconnect RTU Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect RTU Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 2 | Disconnect TCP#1 Alarm | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#1 Alarm","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 3 | Disconnect TCP#1 Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#1 Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 4 | Disconnect TCP#2 Alarm | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#2 Alarm","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 5 | Disconnect TCP#2 Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#2 Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 6 | Disconnect TCP#3 Alarm | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#3 Alarm","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 7 | Disconnect TCP#3 Protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Disconnect TCP#3 Protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 13 | String SOC Imbalance | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"String SOC Imbalance","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 14 | String Count Imbalance | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"String Count Imbalance","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_sys | [System Alarm#2] | bits | --- |  |  |  |  | 15 | Rack Count Imbalance | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Rack Count Imbalance","level":1,"protection":2} |  | V(保固)(一個月)
49 | alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 0 | dcsw_1(s#1(+))_sensing_fail | "0":"False","1":"True" | "1":"red" |  | Rack Common Alarm #1 summary | V(保固)(一個月) | 電池櫃告警1
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 1 | dcsw_2(s#2(+))_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 2 | dcsw_3(main(-))_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 3 | dcsw_1(s#1(+))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 4 | dcsw_2(s#2(+))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 5 | dcsw_3(main(-))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 6 | r_s_comm_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 7 | string_c_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 8 | fuse_1(s#1(+))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 9 | fuse_2(s#2(+))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 10 | fuse_3(main(-))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 11 | dcsw_1(s#1(+))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 12 | dcsw_2(s#2(+))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 13 | dcsw_3(main(-))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 14 | string_v_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_rack_sum | [Rack Common Alarm#1] | bits | --- |  |  |  |  | 15 | rack_pcb_ot | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
50 | alarm2_rack_sum | [Rack Common Alarm#2] | bits | --- |  |  |  |  | 15 | user protection enable | "0":"False","1":"True" | "1":"red" |  | Rack Common Alarm #2 summary | V(保固)(一個月) | 電池櫃告警2
51 | protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 0 | dcsw_1(s#1(+))_sensing_fail | "0":"False","1":"True" | "1":"red" |  | Rack Common Protection #1 summary | V(保固)(一個月) | 電池櫃保護1
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 1 | dcsw_2(s#2(+))_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 2 | dcsw_3(main(-))_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 3 | dcsw_1(s#1(+))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 4 | dcsw_2(s#2(+))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 5 | dcsw_3(main(-))_open_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 6 | r_s_comm_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 7 | string_c_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 8 | fuse_1(s#1(+))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 9 | fuse_2(s#2(+))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 10 | fuse_3(main(-))_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 11 | dcsw_1(s#1(+))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 12 | dcsw_2(s#2(+))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 13 | dcsw_3(main(-))_life_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 14 | string_v_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_rack_sum | [Rack Common Protection#1] | bits | --- |  |  |  |  | 15 | rack_pcb_ot | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
52 | protection2_rack_sum | [Rack Common Protection#2] | bits | --- |  |  |  |  | 15 | user protection enable | "0":"False","1":"True" | "1":"red" |  | Rack Common Protection #2 summary | V(保固)(一個月) | 電池櫃保護2
53 | alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 0 | cell_ov | "0":"False","1":"True" | "1":"red" |  | Rack String Alarm #1 summary | V(保固)(一個月) | 串列告警1
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 1 | cell_uv | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 2 | cv_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 3 | cv_hold | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 4 | cell_ot | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 5 | cell_ut | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 6 | cell_t_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm1_string_sum | [Rack String Alarm#1] | bits | --- |  |  |  |  | 8 | iterative_cell_balancing | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
54 | alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 0 | module_v_difference | "0":"False","1":"True" | "1":"red" |  | Rack String Alarm #2 summary | V(保固)(一個月) | 串列告警2
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 1 | r_m_comm_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 2 | r_m_comm_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 3 | r_m_comm_fail_3 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 4 | all_module_sleep | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 5 | afe_hw_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 6 | mount_check | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 7 | module_pcb_ut | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 8 | r_m_comm_fail_4 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 9 | afe_hw_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm2_string_sum | [Rack String Alarm#2] | bits | --- |  |  |  |  | 10 | afe_hw_fail_3 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
55 | alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 0 | rack_ov | "0":"False","1":"True" | "1":"red" |  | Rack String Alarm #3 summary | V(保固)(一個月) | 串列告警3
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 1 | rack_uv | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 2 | chgoc | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 3 | chgoc_2nd | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 4 | dchgoc | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 5 | dchgoc_2nd | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 6 | charge_current_limit_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm3_string_sum | [Rack String Alarm#3] | bits | --- |  |  |  |  | 7 | discharge_current_limit_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
56 | alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 0 | sensor_v_difference | "0":"False","1":"True" | "1":"red" |  | Rack String Alarm #4 summary | V(保固)(一個月) | 串列告警4
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 1 | sensor_sleep | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 2 | r_sensor_comm_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 3 | r_sensor_comm_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 4 | additional_protection | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 5 | fan_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 6 | powerline_wiring_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 8 | fuse_or_dcsw_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 9 | current stuck | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 10 | currentsensing wire open/short | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 14 | permanent protection | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| alarm4_string_sum | [Rack String Alarm#4] | bits | --- |  |  |  |  | 15 | e-stop protection | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
57 | protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 0 | cell_ov | "0":"False","1":"True" | "1":"red" |  | Rack String Protection #1 summary | V(保固)(一個月) | 串列告警1
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 1 | cell_uv | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 2 | cv_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 3 | cv_hold | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 4 | cell_ot | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 5 | cell_ut | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 6 | cell_t_imb | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection1_string_sum | [Rack String Protection#1] | bits | --- |  |  |  |  | 8 | iterative_cell_balancing | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
58 | protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 0 | module_v_difference | "0":"False","1":"True" | "1":"red" |  | Rack String Protection #2 summary | V(保固)(一個月) | 串列告警2
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 1 | r_m_comm_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 2 | r_m_comm_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 3 | r_m_comm_fail_3 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 4 | all_module_sleep | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 5 | afe_hw_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 6 | mount_check | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 7 | module_pcb_ut | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 8 | r_m_comm_fail_4 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 9 | afe_hw_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection2_string_sum | [Rack String Protection#2] | bits | --- |  |  |  |  | 10 | afe_hw_fail_3 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
59 | protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 0 | rack_ov | "0":"False","1":"True" | "1":"red" |  | Rack String Protection #3 summary | V(保固)(一個月) | 串列告警3
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 1 | rack_uv | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 2 | chgoc | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 3 | chgoc_2nd | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 4 | dchgoc | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 5 | dchgoc_2nd | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 6 | charge_current_limit_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection3_string_sum | [Rack String Protection#3] | bits | --- |  |  |  |  | 7 | discharge_current_limit_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
60 | protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 0 | sensor_v_difference | "0":"False","1":"True" | "1":"red" |  | Rack String Protection #4 summary | V(保固)(一個月) | 串列告警4
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 1 | sensor_sleep | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 2 | r_sensor_comm_fail_1 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 3 | r_sensor_comm_fail_2 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 4 | additional_protection+L192:O193 | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 5 | fan_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 6 | powerline_wiring_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 8 | fuse_or_dcsw_sensing_fail | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 9 | current stuck | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 10 | currentsensing wire open/short | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 14 | permanent protection | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
| protection4_string_sum | [Rack String Protection#4] | bits | --- |  |  |  |  | 15 | e-stop protection | "0":"False","1":"True" | "1":"red" |  |  | V(保固)(一個月)
61 | config1_sys | [System Config#1] | bits | --- |  |  |  |  | 0 | [Partial Operation] Enable | "0":"False","1":"True" |  |  | System Config #1 | V | 系統設定1
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 1 | [System Protection] Fuse or DC Sensing Fail Enable | "0":"False","1":"True" |  |  |  | V
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 7 | Protection Reset Command Reject Enable | "0":"False","1":"True" |  |  |  | V
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 8 | Disconnect RTU Enable | "0":"False","1":"True" |  |  |  | V
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 9 | Disconnect TCP#1 Enable | "0":"False","1":"True" |  |  |  | V
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 10 | Disconnect TCP#2 Enable | "0":"False","1":"True" |  |  |  | V
| config1_sys | [System Config#1] | bits | --- |  |  |  |  | 11 | Disconnect TCP#3 Enable | "0":"False","1":"True" |  |  |  | V
62 | checksum_flash_sys | FLASH | hex | --- | [9 empty] | System Flash Checksum | V | 系統Flash檢查碼
63 | checksum_eeprom_sys | EEPROM | hex | --- | [9 empty] | System EEPROM Checksum | V | 系統EEPROM檢查碼
64 | count_string_min | Partial_Min_String[EA] | number | --- | dec | 0 | [7 empty] | [Partial Operation] Count of Minimum String | V(維運) | 最小String數
65 | v_diff_limit | Partial_Max_Diff[V] | number | --- | V | 0 | [7 empty] | [Partial Operation] Limit of Voltage Difference | V(維運) | 電壓差限制值
66 | bms_time | System[YY-MM-DD hh:mm:ss] | string | --- | [9 empty] | System BMS RTC [YY-MM-DD hh:mm:ss] | V(維運) | BMS時間
67 | alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 0 | dcsw_1(s#1(+))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_sensing_fail","level":1,"protection":2} | [Rack#1][Common] Alarm #1 | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 1 | dcsw_2(s#2(+))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_sensing_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 2 | dcsw_3(main(-))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_sensing_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 3 | dcsw_1(s#1(+))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_open_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 4 | dcsw_2(s#2(+))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_open_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 5 | dcsw_3(main(-))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_open_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 6 | r_s_comm_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_s_comm_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 7 | string_c_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"string_c_imb","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 8 | fuse_1(s#1(+))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_1(s#1(+))_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 9 | fuse_2(s#2(+))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_2(s#2(+))_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 10 | fuse_3(main(-))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_3(main(-))_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 11 | dcsw_1(s#1(+))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_life_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 12 | dcsw_2(s#2(+))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_life_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 13 | dcsw_3(main(-))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_life_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 14 | string_v_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"string_v_imb","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_rack | R[Alarm#1] | bitsArray | --- |  |  |  |  | 15 | rack_pcb_ot | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_pcb_ot","level":1,"protection":2} |  | V(保固)(一個月)
68 | alarm2_rack | R[Alarm#2] | bitsArray | --- |  |  |  |  | 15 | user protection enable | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"user protection enable","level":1,"protection":2} | [Rack#1][Common] Alarm #2 | V(保固)(一個月)
71 | protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 0 | dcsw_1(s#1(+))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_sensing_fail","level":2,"protection":2} | [Rack#1][Common] Protection #1 | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 1 | dcsw_2(s#2(+))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_sensing_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 2 | dcsw_3(main(-))_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_sensing_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 3 | dcsw_1(s#1(+))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_open_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 4 | dcsw_2(s#2(+))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_open_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 5 | dcsw_3(main(-))_open_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_open_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 6 | r_s_comm_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_s_comm_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 7 | string_c_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"string_c_imb","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 8 | fuse_1(s#1(+))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_1(s#1(+))_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 9 | fuse_2(s#2(+))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_2(s#2(+))_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 10 | fuse_3(main(-))_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_3(main(-))_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 11 | dcsw_1(s#1(+))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_1(s#1(+))_life_faile","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 12 | dcsw_2(s#2(+))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_2(s#2(+))_life_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 13 | dcsw_3(main(-))_life_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dcsw_3(main(-))_life_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 14 | string_v_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"string_v_imb","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_rack | R[Protection#1] | bitsArray | --- |  |  |  |  | 15 | rack_pcb_ot | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_pcb_ot","level":2,"protection":2} |  | V(保固)(一個月)
70 | protection2_rack | R[Protection#2] | bitsArray | --- |  |  |  |  | 15 | user protection enable | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"user protection enable","level":2,"protection":2} | [Rack#1][Common] Protection #2 | V(保固)(一個月)
71 | switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 0 | string#1 dc(+) close | "0":"False","1":"True" |  |  | [Rack#1][Common] Switch Control Status | V(保固)(一個月) | Switch 控制狀態
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 1 | string#2 dc(+) close | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 2 | main dc(-) close | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 3 | string#1 dc(+) close command set | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 4 | string#1 dc(+) open command set | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 5 | string#2 dc(+) close command set | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 6 | string#2 dc(+) open command set | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_control_status_rack | R[Con_SW] | bitsArray | --- |  |  |  |  | 7 | wiring check command set | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
72 | switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 0 | string#1 dc(+) close | "0":"False","1":"True" |  |  | [Rack#1][Common] Switch Sensor Status | V(保固)(一個月) | Switch 感測器狀態
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 1 | string#2 dc(+) close | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 2 | main dc(-) close | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 3 | string#1 fuse(+) on | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 4 | string#2 fuse(+) on | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 5 | main fuse(-) on | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 6 | string#1 additional protection | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| switch_sensor_status_rack | R[Sen_SW] | bitsArray | --- |  |  |  |  | 7 | string#2 additional protection | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
73 | P_pos_V_sensor_rack | P+[V](Sensor) | numberArray | --- | V | 0 | scatter | 電壓(V) | [5 empty] | [Rack#1][Common] Voltage (Pack(+) Sensing) | V(保固)(一年) | ?
74 | PowerUV_LV_rack | PowerUV_LV | textArray | --- | [6 empty] | "1":"1200A","2":"700A","3":"500A","4":"200A","5":"0A","6":"-0A","7":"-200A","8":"-500A","9":"-700A","10":"-1200A" |  |  | [Rack#1][Common] Power UV Detect Current Level | V(保固)(一個月)
75 | PowerUV_Open_count_rack | PowerUV_Open[Count] | numberArray | --- | dec | 0 | scatter | 數量 | [5 empty] | [Rack#1][Common] Power UV Detect DC Contactor Open Count | V(保固)(一個月)
76 | PowerUV_Close_count_rack | PowerUV_Close[Count] | numberArray | --- | dec | 0 | scatter | 數量 | [5 empty] | [Rack#1][Common] Power UV Detect DC Contactor Close Count | V(保固)(一個月)
77 | checksum_flash_rack | FLASH | hexArray | --- | [9 empty] | [Rack#1][Common] Flash Checksum | V
78 | checksum_eeprom_rack | EEPROM | hexArray | --- | [9 empty] | [Rack#1][Common] EEPROM Checksum | V
79 | mode_string | S#[Mode] | textArray | --- | [6 empty] | "0":"None","1":"Initialize","2":"Offline -DC-Open","3":"Offline -DC-Close" |  |  | [Rack#1][String#1] Mode | V(保固)(一個月) | 電池櫃狀態
80 | alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 0 | cell_ov | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ov","level":1,"protection":2} | [Rack#1][String#1] Alarm #1 | V(保固)(一個月) | 串列告警1
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 1 | cell_uv | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_uv","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 2 | cv_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cv_imb","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 3 | cv_hold | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cv_hold","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 4 | cell_ot | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ot","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 5 | cell_ut | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ut","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 6 | cell_t_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_t_imb","level":1,"protection":2} |  | V(保固)(一個月)
| alarm1_string | S#[Alarm#1] | bitsArray | --- |  |  |  |  | 8 | iterative_cell_balancing | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"iterative_cell_balancing","level":1,"protection":2} |  | V(保固)(一個月)
81 | alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 0 | module_v_difference | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"module_v_difference","level":1,"protection":2} | [Rack#1][String#1] Alarm #2 | V(保固)(一個月) | 串列告警2
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 1 | r_m_comm_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_1","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 2 | r_m_comm_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_2","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 3 | r_m_comm_fail_3 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_3","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 4 | all_module_sleep | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"all_module_sleep","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 5 | afe_hw_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_1","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 6 | mount_check | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"mount_check","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 7 | module_pcb_ut | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"module_pcb_ut","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 8 | r_m_comm_fail_4 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_4","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 9 | afe_hw_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_2","level":1,"protection":2} |  | V(保固)(一個月)
| alarm2_string | S#[Alarm#2] | bitsArray | --- |  |  |  |  | 10 | afe_hw_fail_3 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_3","level":1,"protection":2} |  | V(保固)(一個月)
82 | alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 0 | rack_ov | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_ov","level":1,"protection":2} | [Rack#1][String#1] Alarm #3 | V(保固)(一個月) | 串列告警3
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 1 | rack_uv | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_uv","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 2 | chgoc | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"chgoc","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 3 | chgoc_2nd | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"chgoc_2nd","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 4 | dchgoc | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dchgoc","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 5 | dchgoc_2nd | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dchgoc_2nd","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 6 | charge_current_limit_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"charge_current_limit_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm3_string | S#[Alarm#3] | bitsArray | --- |  |  |  |  | 7 | discharge_current_limit_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"discharge_current_limit_fail","level":1,"protection":2} |  | V(保固)(一個月)
83 | alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 0 | sensor_v_difference | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"sensor_v_difference","level":1,"protection":2} | [Rack#1][String#1] Alarm #4 | V(保固)(一個月) | 串列告警4
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 1 | sensor_sleep | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"sensor_sleep","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 2 | r_sensor_comm_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_sensor_comm_fail_1","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 3 | r_sensor_comm_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_sensor_comm_fail_2","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 4 | additional_protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"additional_protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 5 | fan_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fan_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 6 | powerline_wiring_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"powerline_wiring_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 8 | fuse_or_dcsw_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_or_dcsw_sensing_fail","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 9 | current stuck | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"current stuck","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 10 | currentsensing wire open/short | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"currentsensing wire open/short","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 14 | permanent protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"permanent protection","level":1,"protection":2} |  | V(保固)(一個月)
| alarm4_string | S#[Alarm#4] | bitsArray | --- |  |  |  |  | 15 | e-stop protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"e-stop protection","level":1,"protection":2} |  | V(保固)(一個月)
84 | protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 0 | cell_ov | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ov","level":2,"protection":2} | [Rack#1][String#1] Protection #1 | V(保固)(一個月) | 串列保護1
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 1 | cell_uv | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_uv","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 2 | cv_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cv_imb","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 3 | cv_hold | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cv_hold","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 4 | cell_ot | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ot","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 5 | cell_ut | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_ut","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 6 | cell_t_imb | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_t_imb","level":2,"protection":2} |  | V(保固)(一個月)
| protection1_string | S#[Protection#1] | bitsArray | --- |  |  |  |  | 8 | iterative_cell_balancing | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"iterative_cell_balancing","level":2,"protection":2} |  | V(保固)(一個月)
85 | protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 0 | module_v_difference | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"module_v_difference","level":2,"protection":2} | [Rack#1][String#1] Protection #2 | V(保固)(一個月) | 串列保護2
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 1 | r_m_comm_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_1","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 2 | r_m_comm_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_2","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 3 | r_m_comm_fail_3 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_3","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 4 | all_module_sleep | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"all_module_sleep","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 5 | afe_hw_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_1","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 6 | mount_check | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"mount_check","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 7 | module_pcb_ut | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"module_pcb_ut","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 8 | r_m_comm_fail_4 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_4","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 9 | afe_hw_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_2","level":2,"protection":2} |  | V(保固)(一個月)
| protection2_string | S#[Protection#2] | bitsArray | --- |  |  |  |  | 10 | afe_hw_fail_3 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail_3","level":2,"protection":2} |  | V(保固)(一個月)
86 | protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 0 | rack_ov | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_ov","level":2,"protection":2} | [Rack#1][String#1] Protection #3 | V(保固)(一個月) | 串列保護3
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 1 | rack_uv | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"rack_uv","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 2 | chgoc | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"chgoc","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 3 | chgoc_2nd | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"chgoc_2nd","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 4 | dchgoc | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dchgoc","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 5 | dchgoc_2nd | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"dchgoc_2nd","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 6 | charge_current_limit_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"charge_current_limit_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection3_string | S#[Protection#3] | bitsArray | --- |  |  |  |  | 7 | discharge_current_limit_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"discharge_current_limit_fail","level":2,"protection":2} |  | V(保固)(一個月)
87 | protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 0 | sensor_v_difference | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"sensor_v_difference","level":2,"protection":2} | [Rack#1][String#1] Protection #4 | V(保固)(一個月) | 串列保護4
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 1 | sensor_sleep | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"sensor_sleep","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 2 | r_sensor_comm_fail_1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_sensor_comm_fail_1","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 3 | r_sensor_comm_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_sensor_comm_fail_2","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 4 | additional_protection+L192:O193 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"additional_protection","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 5 | fan_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fan_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 6 | powerline_wiring_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"powerline_wiring_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 8 | fuse_or_dcsw_sensing_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"fuse_or_dcsw_sensing_fail","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 9 | current stuck | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"current stuck","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 10 | currentsensing wire open/short | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"currentsensing wire open/short","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 14 | permanent protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"permanent protection","level":2,"protection":2} |  | V(保固)(一個月)
| protection4_string | S#[Protection#4] | bitsArray | --- |  |  |  |  | 15 | e-stop protection | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"e-stop protection","level":2,"protection":2} |  | V(保固)(一個月)
88 | control_status_string | S#[Con] | bitsArray | --- |  |  |  |  | 0 | fan | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列控制狀態
89 | v_string | S#[V](Sensor) | numberArray | --- | V | 1 | scatter | 電壓(V) | [6 empty] | V(保固)(一年) | 串列電壓
90 | i_string | S#[A](Sensor) | numberArray | --- | A | 1 | scatter | 電流(A) | [6 empty] | V(保固)(一個月) | 串列電流
91 | soc_string | S#_SOC[%] | numberArray | --- | % | 1 | scatter | SOC(%) | [6 empty] | V(保固)(一年) | 串列SOC
92 | soh_string | S#_SOH[%] | numberArray | --- | % | 1 | scatter | SOH(%) | [6 empty] | V | 串列SOH
93 | i_chg_limit_string | S#_Limit[A](Chg) | numberArray | --- | A | 1 | scatter | 電流(A) | [6 empty] | V | 串列充電電流限制
94 | i_dischg_limit_string | S#_Limit[A](Dchg) | numberArray | --- | A | 1 | scatter | 電流(A) | [6 empty] | V | 串列放電電流限制
95 | p_chg_limit_string | S#_Limit[kW](Chg) | numberArray | --- | kW | 2 | scatter | 功率(kW) | [6 empty] | V | 串列功率電流限制
96 | p_dischg_limit_string | S#_Limit[kW](Dchg) | numberArray | --- | kW | 2 | scatter | 功率(kW) | [6 empty] | V | 串列功率電流限制
97 | kwh_chg_string | S#_Chg[kWh] | numberArray | --- | kWh | 3 | bar | 電能(kWh) | [6 empty] | V(保固)(一年) | 串列充電電能
98 | kwh_dischg_string | S#_Dchg[kWh] | numberArray | --- | kWh | 3 | bar | 電能(kWh) | [6 empty] | V(保固)(一年) | 串列放電電能
99 | module_power_off_string | S#_Power_Off[M#] | numberArray | --- | dec | 0 | scatter | 數量 | [6 empty] | V | 串列模組斷電位置
100 | module_comm_fault_string | S#_CommF[M#] | numberArray | --- | dec | 0 | scatter | 數量 | [6 empty] | V | 串列模組通訊錯誤位置
101 | cv_diff_string | S#_[CV](Max(Diff)) | numberArray | --- | V | 3 | scatter | 電壓(V) | [6 empty] | V | 串列最高單電池電壓差
102 | cv_max_string | S#_[CV](Max(1st)) | numberArray | --- | V | 3 | scatter | 電壓(V) | [6 empty] | V(保固)(一個月) | 串列最高單電池電壓(#電池模組,#單電池)
103 | cv_max_mIndex_string | S#_Loc[M#] | numberArray | --- | dec | 0 | [8 empty] | V
104 | cv_max_cIndex_string | S#_Loc[C#] | numberArray | --- | dec | 0 | [8 empty] | V
105 | cv_min_string | S#_[CV](Min(1st)) | numberArray | --- | V | 3 | scatter | 電壓(V) | [6 empty] | V(保固)(一個月) | 串列最低單電池電壓(#電池模組,#單電池)
106 | cv_min_mIndex_string | S#_Loc[M#] | numberArray | --- | dec | 0 | [8 empty] | V
107 | cv_min_cIndex_string | S#_Loc[C#] | numberArray | --- | dec | 0 | [8 empty] | V
108 | ct_string | S#_[CT](Avg) | numberArray | --- | ℃ | 2 | scatter | 溫度(°C) | [6 empty] | V | 串列平均單電池溫度
109 | ct_max_string | S#_[CT](Max(1st)) | numberArray | --- | ℃ | 2 | scatter | 溫度(°C) | [6 empty] | V(保固)(一年) | 串列最高單電池溫度(#電池模組,#單電池)
110 | ct_max_mIndex_string | S#_Loc[M#] | numberArray | --- | dec | 0 | [8 empty] | V
111 | ct_max_cIndex_string | S#_Loc[C#] | numberArray | --- | dec | 0 | [8 empty] | V
112 | ct_min_string | S#_[CT](Min(1st)) | numberArray | --- | ℃ | 2 | scatter | 溫度(°C) | [6 empty] | V(保固)(一年) | 串列最低單電池溫度(#電池模組,#單電池)
113 | ct_min_mIndex_string | S#_Loc[M#] | numberArray | --- | dec | 0 | [8 empty] | V
114 | ct_min_cIndex_string | S#_Loc[C#] | numberArray | --- | dec | 0 | [8 empty] | V
115 | sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 0 | Rx Invalid | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列感測器狀態
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 1 | RAM_A | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 2 | DF_A | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 3 | RAM_B | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 4 | DF_B | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 5 | Code Checksum | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 6 | Rx Time out | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 7 | Rx Checksum | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| sensor_status_string | S#_Reg[Sensor] | bitsArray | --- |  |  |  |  | 8 | Over Current Range | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
116 | module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 0 | Rx Idle | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列模組狀態(Scan)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 1 | Rx Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 2 | Rx Error | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 3 | Rx Overflow | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 4 | Rx Command | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 5 | Rx Register | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 6 | Rx Datacheck | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_scan_string | S#_M_Reg[Scan] | bitsArray | --- |  |  |  |  | 7 | Rx PEC | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
117 | module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 0 | Rx Idle | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列模組狀態(Balancing)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 1 | Rx Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 2 | Rx Error | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 3 | Rx Overflow | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 4 | Rx Command | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 5 | Rx Register | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 6 | Rx Datacheck | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_balance_string | S#_M_Reg[Balancing] | bitsArray | --- |  |  |  |  | 7 | Rx PEC | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
118 | module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 0 | Rx Idle | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列模組狀態(Address)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 1 | Rx Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 2 | Rx Error | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 3 | Rx Overflow | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 4 | Rx Command | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 5 | Rx Register | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 6 | Rx Datacheck | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_address_string | S#_M_Reg[Address] | bitsArray | --- |  |  |  |  | 7 | Rx PEC | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
119 | module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 0 | Rx Idle | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列模組狀態(Voltage)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 1 | Rx Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 2 | Rx Error | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 3 | Rx Overflow | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 4 | Rx Command | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 5 | Rx Register | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 6 | Rx Datacheck | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_voltage_string | S#_M_Reg[Voltage] | bitsArray | --- |  |  |  |  | 7 | Rx PEC | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
120 | module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 0 | Rx Idle | "0":"False","1":"True" |  |  |  | V(保固)(一個月) | 串列模組狀態(Temperature)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 1 | Rx Stop | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 2 | Rx Error | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 3 | Rx Overflow | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 4 | Rx Command | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 5 | Rx Register | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 6 | Rx Datacheck | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
| module_status_temp_string | S#_M_Reg[Temperature] | bitsArray | --- |  |  |  |  | 7 | Rx PEC | "0":"False","1":"True" |  |  |  | V(保固)(一個月)
121 | dist_under_20mV_string | S#_DIST[Under 20mV] | numberArray | --- | % | 2 | scatter | % | [6 empty] | V(報表)
122 | dist_under_VImb_A_string | S#_DIST[Under V-Imb A] | numberArray | --- | % | 2 | scatter | % | [6 empty] | V(報表)
123 | dist_under_VImb_P_string | S#_DIST[Under V-Imb P] | numberArray | --- | % | 2 | scatter | % | [6 empty] | V(報表)
124 | dist_under_VImb_P_More_string | S#_DIST[V-Imb P or More] | numberArray | --- | % | 2 | scatter | % | [6 empty] | V(報表)
125 | cell_balance_count_max_string | S#_Bal[Cnt](Max) | numberArray | --- | dec | 0 | scatter | 數量 | [6 empty] | V(報表)
126 | cell_balance_count_max_mIndex_string | S#_Loc[M#] | numberArray | --- | dec | 0 | scatter | 數量 | [6 empty] | V(報表)
127 | cell_balance_count_max_cIndex_string | S#_Loc[C#] | numberArray | --- | dec | 0 | scatter | 數量 | [6 empty] | V(報表)
128 | v_module | Module[V] | numberArray2 | --- | V | 3 | scatter | 電壓(V) | [5 empty] | [Module#1] Module Voltage | V | 電池模組電壓
129 | v_cell | Cell#[V] | numberArray3 | --- | V | 3 | scatter | 電壓(V) | [5 empty] | [Module#v_cell] Cell# | V | 單電池電壓
130 | temp1_module | Temp#01[T] | numberArray2 | --- | ℃ | 2 | scatter | 溫度(°C) | [5 empty] | [Module#1] Module Temperature#01 | V | 電池模組溫度1
131 | temp2_module | Temp#02[T] | numberArray2 | --- | ℃ | 2 | scatter | 溫度(°C) | [5 empty] | [Module#1] Module Temperature#02 | V | 電池模組溫度2
132 | protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 0 | cell_v_hold | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_v_hold","level":2,"protection":2} | [Module#1] Protection | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 1 | module_v_difference | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"module_v_difference","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 2 | r_m_comm_fail_2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"r_m_comm_fail_2","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 3 | mount_check | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"mount_check","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 4 | fan_fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"cell_v_hold","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 5 | afe_hw_fail1 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail1","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 6 | afe_hw_fail2 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail2","level":2,"protection":2} |  | V
| protection_module | [Protection] | bitsArray2 | --- |  |  |  |  | 7 | afe_hw_fail3 | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"afe_hw_fail3","level":2,"protection":2} |  | V
133 | cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 0 | Cell#1 Balancing Set | "0":"False","1":"True" |  |  | [Module#1] Cell Balancing Status | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 1 | Cell#2 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 2 | Cell#3 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 3 | Cell#4 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 4 | Cell#5 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 5 | Cell#6 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 6 | Cell#7 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 7 | Cell#8 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 8 | Cell#9 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 9 | Cell#10 Balancing Set | "0":"False","1":"True" |  |  |  | V
| cell_balance_module | [Balancing] | bitsArray2 | --- |  |  |  |  | 10 | Cell#11 Balancing Set | "0":"False","1":"True" |  |  |  | V
134 | ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 0 | Auxiliary#0 On | "0":"False","1":"True" |  |  | [Module#1] External Sensor Status | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 1 | Auxiliary#1 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 2 | Auxiliary#2 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 3 | Auxiliary#3 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 4 | Auxiliary#4 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 5 | Auxiliary#5 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 6 | Auxiliary#6 On | "0":"False","1":"True" |  |  |  | V
| ext_sen_module | [Ext_Sen] | bitsArray2 | --- |  |  |  |  | 7 | Auxiliary#7 On | "0":"False","1":"True" |  |  |  | V
135 | Afe_Diag1 | Afe_Diag#01 | hexArray2 | --- | [9 empty] | [Module#1] Diagnosis Status #1 | V
136 | Afe_Diag2 | Afe_Diag#02 | hexArray2 | --- | [9 empty] | [Module#1] Diagnosis Status #2 | V
137 | Afe_Diag3 | Afe_Diag#03 | hexArray2 | --- | [9 empty] | [Module#1] Diagnosis Status #3 | V
138 | Afe_Diag4 | Afe_Diag#04 | hexArray2 | --- | [9 empty] | [Module#1] Diagnosis Status #4 | V
139 | config2_sys | [System Config#2] | bits | --- |  |  |  |  | 0 | [E-Stop] Partial Operation Enable | "0":"False","1":"True" |  |  | system config #2 | V
| config2_sys | [System Config#2] | bits | --- |  |  |  |  | 1 | [E-Stop] Protection Enable | "0":"False","1":"True" |  |  |  | V
| config2_sys | [System Config#2] | bits | --- |  |  |  |  | 2 | [E-Stop] SPD Enable | "0":"False","1":"True" |  |  |  | V
| config2_sys | [System Config#2] | bits | --- |  |  |  |  | 3 | [E-Stop] Permanent Protection Enable | "0":"False","1":"True" |  |  |  | V

## UPS資料表
Index | tag | name | tagType | error | unit | round | plotType | y_title | bitIndex | bitName | translate | color | alarm | Data | EMS | 名稱備註
1 | bat_status | 電池狀態 | text | --- | [6 empty] | "1":"unknown","2":"batteryNormal","3":"batteryLow" | "3":"red" |  | Battery Status | v | Integer Value: unknown(1), batteryNormal(2), BatteryLow(3)
2 | bat_soc | SOC | number | --- | % | 1 | scatter | SOC(%) | [5 empty] | Battery Capacity | v
3 | bat_v | 電池電壓 | number | --- | Vdc | 2 | scatter | 電壓(V) | [5 empty] | Battery Voltage | v
4 | bat_temp | 電池溫度 | number | --- | ℃ | 1 | scatter | 溫度(°C) | [5 empty] | Battery Temperature | v
5 | bat_a | 電池電流 | number | --- | A | 1 | scatter | 電流(A) | [5 empty] | Battery Current | v
6 | in_v | 輸入電壓 | number | --- | Vac | 1 | scatter | 電壓(V) | [5 empty] | Input Line Voltage | v
7 | in_f | 輸入頻率 | number | --- | Hz | 1 | scatter | 頻率(Hz) | [5 empty] | Input Frequency | v
8 | in_a | 輸入電流 | number | --- | A | 1 | scatter | 電流(A) | [5 empty] | Input Current | v
9 | in_p | 輸入實功 | number | --- | W | 1 | scatter | 實功(W) | [5 empty] | Input True Power | v
10 | out_status | 輸出狀態 | text | --- | [6 empty] | "1":"unknown","2":"onLine","3":"onBattery","4":"onBoost","5":"sleeping","6":"onBypass","7":"rebooting","8":"standBy","9":"onBuck" |  |  | Output Status | v | Integer Value: unknown(1), onLine(2), onBattery(3), onBoost(4), sleeping(5), onBypass(6), rebooting(7), standBy(8), onBuck(9)
11 | out_v | 輸出電壓 | number | --- | Vac | 1 | scatter | 電壓(V) | [5 empty] | Output Voltage | v
12 | out_f | 輸出頻率 | number | --- | Hz | 1 | scatter | 頻率(Hz) | [5 empty] | Output Frequency | v
13 | out_a | 輸出電流 | number | --- | A | 1 | scatter | 電流(A) | [5 empty] | Output Current | v
14 | out_p | 輸出實功 | number | --- | W | 1 | scatter | 實功(W) | [5 empty] | Output True Power | v
15 | dc_rre |  |  | --- | [9 empty] | DC and Rectifier Status RecRotError |  | Integer Value: yes(14),no(16)
16 | dc_lbs |  |  | --- | [9 empty] | DC and Rectifier Status LowBatteryShutdown |  | Integer Value: yes(14),no(16)
17 | dc_lb |  |  | --- | [9 empty] | DC and Rectifier Status LowBattery |  | Integer Value: yes(14),no(16)
18 | dc_iao |  |  | --- | [9 empty] | DC and Rectifier Status InAndOut |  | Integer Value: threeInOneOut(2),threeInThreeOut(3)
19 | dc_bs |  |  | --- | [9 empty] | DC and Rectifier Status BatteryStatus |  | Integer Value: backup(4),acnormal(5)
20 | dc_cs |  |  | --- | [9 empty] | DC and Rectifier Status ChargeStatus |  | Integer Value: boost(6),float(7),no(16)
21 | dc_ro |  |  | --- | [9 empty] | DC and Rectifier Status RecOperating |  | Integer Value: yes(14),no(16)
22 | ups_bef |  |  | --- | [9 empty] | UPS Status Bypass Freqency Fail |  | Integer Value: yes(14),no(16)
23 | ups_mbb |  |  | --- | [9 empty] | UPS Status Manual Bypass Breaker |  | Integer Value: close(8),open(9)
24 | ups_ac |  |  | --- | [9 empty] | UPS Status AC Status |  | Integer Value: normal(10),abnormal(11)
25 | ups_sm |  |  | --- | [9 empty] | UPS Status Static Switch Mode |  | Integer Value: invermode(12),bypassmode(13)
26 | ups_io |  |  | --- | [9 empty] | UPS Status Inverter Operating |  | Integer Value: yes(14),no(16)
27 | alarm | 告警 | bits | --- |  |  |  |  | 0 | Utility Fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Utility Fail","level":1,"protection":0} | ALARM | v | bit 00 : Utility Fail bit 01 : UPS Failed bit 02 : Test in Progress bit 03 : Shutdown Active bit 04 : Beeper On
| alarm | 告警 | bits | --- |  |  |  |  | 1 | UPS Failed | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"UPS Failed","level":1,"protection":0} |  | v
| alarm | 告警 | bits | --- |  |  |  |  | 2 | Test in Progress | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Test in Progress","level":1,"protection":0} |  | v
| alarm | 告警 | bits | --- |  |  |  |  | 3 | Shutdown Active | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Shutdown Active","level":1,"protection":0} |  | v
| alarm | 告警 | bits | --- |  |  |  |  | 4 | Beeper On | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Beeper On","level":1,"protection":0} |  | v
28 | fault | 故障 | bits | --- |  |  |  |  | 0 | Fault Status Emergency Stop | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Emergency Stop","level":2,"protection":0} | FAULT | v | bit 00 : Fault Status Emergency Stop bit 01 : Fault Status High DC Shutdown bit 02 : Fault Status Bypass Breaker bit 03 : Fault Status Over Load bit 04 : Fault Status Inverter Output Fail bit 05 : Fault Status Over Temperature bit 06 : Fault Status Short Circuit
| fault | 故障 | bits | --- |  |  |  |  | 1 | Fault Status High DC Shutdown | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status High DC Shutdown","level":2,"protection":0} |  | v
| fault | 故障 | bits | --- |  |  |  |  | 2 | Fault Status Bypass Breaker | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Bypass Breaker","level":2,"protection":0} |  | v
| fault | 故障 | bits | --- |  |  |  |  | 3 | Fault Status Over Load | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Over Load","level":2,"protection":0} |  | v
| fault | 故障 | bits | --- |  |  |  |  | 4 | Fault Status Inverter Output Fail | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Inverter Output Fail","level":2,"protection":0} |  | v
| fault | 故障 | bits | --- |  |  |  |  | 5 | Fault Status Over Temperature | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Over Temperature","level":2,"protection":0} |  | v
| fault | 故障 | bits | --- |  |  |  |  | 6 | Fault Status Short Circuit | "0":"False","1":"True" | "1":"red" | {"value":1,"operate":"=","event":"Fault Status Short Circuit","level":2,"protection":0} |  | v